# Plans & Performance

## PLANS FOR UNDERTAKING LOAD RESEARCH

Requirement in the Guidelines:

Plans for undertaking load research to determine the load profile of consumers supplied under each tariff

(Guidelines – 10a)

APCPDCL’s Response.

APCPDCL has furnished profile of the consumers of different classes with improved facilities of billing and load monitoring. APCPDCL has established a computerized load monitoring center as well as billing center at Corporate Office and the Load Research activity has been stepped up to meet the full requirements of guidelines of the Hon’ble Commission in this regard.

Presently the load profiling and monitoring is being done at the 33/11KV substations mainly for agricultural load because of the importance of this category of consumers in the total energy consumption and also its importance in arriving at the energy losses.

APCPDCL has provided metering arrangements on LV side 7964 Nos distribution transformers, feeding predominantly agricultural loads, including 6262 Nos distribution transformers feeding exclusively agricultural loads. The monthly readings of these meters are regularly taken data is analyzed to assess the realistic level of agricultural consumption as per the directive of the Commission.

APCPDCL is already having sophisticated metering arrangements for the HT services. All these meters have the facility of data retrieval through MRI. APCPDCL is under taking the load research of all the HT services from the data retrieved through MRIs. In addition to the above APCPDCL have also taken up energy audit in 177 nos. of Industrial feeders to assess the commercial loss levels and locating the pockets of theft for further physical inspection and to detect the pilferage. APCPDCL is also studying the feasibility of introducing remote meter reading, if considered economically viable. The company has already started remotely monitoring the energy flow data input in order to assess the levels of commercial losses and monitoring of Interruptions and Breakdowns.

Regarding the load profile of different classes of metered consumers, it is to be stated that the metering is already available for these consumers and meter readings are being taken regularly. The details of monthly energy consumption and the connected load of various categories is being submitted regularly in the sales data base in the format prescribed by the Hon’ble Commission. Thus APCPDCL is able to provide a reasonably realistic profile of the various categories of consumers considering the class load factor of the various classes of consumers.

The profile of the various classes of consumers under different sub-categories are furnished, in the prescribed formats, along with the tariff application.

For understanding the load profile of the consumers under each tariff, a mechanism was developed to receive the daily curves for 10 nos. 11KV feeders, feeding predominantly   1) Domestic 2) Commercial 3) Agricultural 4) LT Industries  5) HT Industries and         6) HT Commercial.

## PLANS FOR IMPROVING THE SYSTEM POWER FACTOR

Requirement in the Guidelines :

Plans to improve the system power factor by providing an incentive for consumers to install correction capacitors. (Guidelines – 10b).

APCPDCL’s Response

All the consumers using induction motors have to install capacitors of appropriate rating to  improve the power factor of their loads.

All the HT consumers & LT III B consumers are levied capacitor surcharge if the monthly  power factor recorded is less than 0.9.

For consumers other than the above, if the capacitors of appropriate rating are not provided 25% capacitor surcharge is being levied on the monthly-billed amount.

In respect of agricultural consumers, counseling is being done through local offices for erection of  friction less foot valves, use of PVC pipes etc to improve the efficiency of pumping.

2MVAR capacitor banks at 33/11kv substations and 600KVAR capacitors on 11kv feeders are being extensively used to correct the system power factor.

## PLANS FOR DETERMINING THE RELATIONSHIP BETWEEN Kwh CONSUMED AND CONNECTED LOADS

Requirement in Guidelines

Plans for determining the relationship between kWh consumed and connected loads on which unmetered charges are levied. (Guidelines 10 c)

APCPDCL’s Response:

The methodology prescribed by Hon’ble APERC for estimation of agricultural consumption in CPDCL is being adopted. The assessment of consumption for the un-metered LT agricultural consumers is being done based on the readings of the meters provided on the sample agricultural DTRs. These consumers are given three-phase supply for regulated hours per day as per the approval of the Hon’ble Commission. Hence all the agricultural pump sets are assumed to use power during the three phase supply timings.

The information of the connected load (in HP) and the recorded consumption as per the LV side meter readings of agricultural DTRs is used to estimate the    KWH / HP of the agricultural load, from DTR level to Mandal and hence district level for assessment of agricultural consumption.

The no of agricultural services being considered are as per the census study.

All effort are being made by CPDCL to improve the coverage ratio and quality ratio in respect of sampling LV side DTR meter readings for arriving the accurate estimate on agricultural consumption to the extent possible.

## PROGRAMME FOR CONVERTING UNMETERED CONNECTIONS TO METERED SUPPLY

Requirement in the Guidelines:

Programme for converting unmetered connections to metered supply, together with investment needed. (Guidelines 10d).

APCPDCL’s Response

APCPDCL submits that pursuant to the GoAP policy of free power to agricultural category, the comprehensive metering plan of agricultural services will be taken up as per the policy decided by the GoAP, under the guidance of the   Hon’ble Commission.

## METHOD OF ASSESSING CONSUMPTION WHEN METERS ARE NOT INSTALLED / DEFECTIVE

Requirement in the Guidelines

Method of assessing consumption when meter is not installed or is defective, together  with basis for such assessment (Guidelines 10 e).

CPDCL’s Response

The methodology provided under clause 22.3.3 of the existing Terms and Conditions of Supply is adopted for assessment of consumption of a category of consumer, necessitated due to metering not being available or defective, till the draft GTCS is finalized by the Hon’ble Commission.

## PLANS FOR RATIONALISING EXISTING MANPOWER

Requirement in the Guidelines

Plans, both short-term and long-term for rationalization of existing manpower (Guidelines 10f)

APCPDCL’s  Response:

In order to retain the existing trained manpower the Assistant Engineers, Sub-Engineers and LDCs who were appointed on Contract basis are regularized based on the performance report of past two years.  In order to improve the Operational performance and to optimize/rationalize the workload and to provide better service to consumers, 35 Additional Operation Sections were formed by bifurcation of the overloaded Sections.  It was felt that necessary that there is requirement of additional Sub-Engineer posts for providing necessary support to the Sections, Sub-Divisions and Divisions.   In this regard proposals were called for from the Field Offices.  For better monitoring of the Operation and Revenue activities two new Operation Divisions one at Medchal and another at Toopran were formed for which additional 27 Nos. posts were newly created.

To increase the accountability the Audit Wing was strengthened by entrusting the Audit activities of the 10 Operation Circles to Chartered Accountants for continuous auditing of the activities and for keeping a vigil on the procedures in vogue and for curtailing the wasteful expenditure.  The Contract Agreement has been extended upto 31.03.2006.  In order to bring out competency, improve internal efficiency and practice latest business standards personnel having higher qualifications are being recruited from open market.

The Private Accounting Agencies are entrusted with the works of Billing, Issue of D-list, other non-routine works on contract basis as a measure of cost reduction.  In the event of vacancies, from time to time based on the necessity certain works such as Driving, Typing and Office Assistance are being entrusted to private agencies to carry out the works on yearly contract basis, to avoid dislocation of works.  Steps are taken that the contractor employees personnel have adequate qualification and checks are done about the compliance of the statutory obligations.    In order to comply with the direction of the APERC and for providing better Consumer Service separate Consumer Service Centers were formed for each Operation Sub-Division and all consumer related activities are undertaken in these centers by the Private Agency.

It is decided to implement SAP Modules for HR, Finance and Material Management for improving internal efficiency, reduction of Manpower simplification of works and for better accountability.  With the Transfer of Procurement and Bulk Supply of Electricity and Trading of Electricity and allocation of Power Purchase Agreements from APTRANSCO to APCPDCL, 81 Posts in various cadres such as Superintending Engineers, Divisional Engineers, Asst. Divisional Engineers, AEs/AAEs, G.M., SAO, AO, AAO, AS, PO and JPO etc., were created to the works of Power Purchase Agreements(IPC), Load Research Monitoring, Quality Control etc.

The training needs of all the employees have been assessed and need based trainings are being conducted to systematically train all the employees of APCPDCL.  On the name of Training on Wheels conducted training programmes at Divisions.  Soft skills have been developed to cater to the changed scenario and many programmes are conducted to improve the work culture.  It is proposed to decentralize the training activity and in this line programmes are scheduled in Rural Sections/Divisions.  All the concerned employees are being given training for using the SAP Modules, which are to be rolled out shortly.

## Expansion Plan for Capital Investments

Requirement in the Guidelines

Expansion plan for all capital investment (Guide Lines 10g)

APCPDCL’s Response

## As on 31st March 2005 the existing substations, lines and other relevant statistics of APCPDCL

## Table 10.g.1 Existing Lines and Substations:

| Sl. No. | Particulars | Unit | Quantity |
| --- | --- | --- | --- |
| 1. | 33 KV Substations | Nos. | 951 |
| 2. | 33 KV Lines | KM | 11420 |
| 3. | 11 KV Lines | KM | 67933 |
| 4. | Distribution Transformers | Nos. | 148581 |
| 5. | Towns Electrified | Nos. | 74 |
| 6. | Villages Electrified | Nos. | 6496 |
| 7. | Hamlets Electrified | Nos. | 7659 |
| 8. | Dalitwadas Electrified | Nos. | 12105 |
| 9. | Weaker Section Colonies Electrified | Nos. | 5806 |

During 2005-06, the programme of addition of substations is as follows:

Table 10.g.2 Planned Substations

| Voltage (KV) | Nos. of Substations |
| --- | --- |
| 33 KV / 11 KV | 82 |

## Table 10.g.4 Planned Release of Services to Weaker Sections

| Category | Number of Connections |
| --- | --- |
| Hamlets | 323 |
| Dalitwadas | 933 |
| Weaker Section Colonies | 754 |
| Tribal Hamlets | 475 |
| Agricultural pumpsets | 16500 |
| Laying of conventional lines in villages with SPV panels | - |

This investment is broadly meant for the following purposes:

# Rs. in crores

| Sl. No | Investment | 2005-06 | 2006-07 |
| --- | --- | --- | --- |
| 1 | SI (New) | 19.27 | 71.97 |
| 2 | PFC (Hyd City Scheme) | 50 | 108 |
| 3 | Pumpset Energisation | 15 | 15 |
| 4 | Metering Schemes | 50 | 32 |
| 5 | Material Schemes | 15 | 45 |
| 6 | SI Transformers | 5 | 10 |
| 7 | Rural Electrification (RGGVY) | 58.65 | 58.65 |
| 8 | APDRP Town schemes | 49.5 | - |
| 9 | APDRP Hyderabad scheme | 12.5 | - |
| 10 | HVDS Agriculture (New) | 40 | 109 |
| 11 | Release of Services | 48.45 | 59.7 |
| 12 | T & D | 50 | 55 |
|  | Total | 413.37 | 564.32 |

## NUMBER AND DURATION OF INTERRUPTIONS ON THE NETWORK

Requirement in the Guidelines:

Number and duration of supply interruptions on the distribution networks, separately for 33KV, 11KV and LT systems. Details of steps proposed to improve performance and monitoring. (Guidelines – 11a).

APCPDCL’s Response:

The number and duration of interruptions and breakdowns, recorded at substations for all 33KV and 11KV feeders are given in table 11a1 and table 11a2 respectively. Regarding interruptions on the LT system, the complaints received at FOC (Fuse of Calls) centers are categorized under the following heads:

Service wire defects

LT fuse blown

LT line fault

Horn gap fuse blown

DTR failure

Each circle of APCPDCL has a control room for load monitoring and in turn to report to the LMC located at Corporate office for monitoring the interruptions of 33KV, 11KV and LT distribution networks as well as the rectification measures that were carried out.

The LMC monitors power supply position round the clock in APCPDCL.

APCPDCL has fixed the time limits within which the restoration of normalcy of lines/equipment are to be achieved. It is the responsibility of the field officers to adhere to these standards. The field officers also conduct pre-monsoon inspections and rectify and defects noticed by them during this process. The projects wing monitor overloaded lines and equipment and take necessary steps to strengthen or expand the net work wherever required. Electrical clearances between trees and line/equipment are checked regularly to minimize the interruptions due to fouling of branches with live conductor etc. The APCPDCL also provided additional vehicles to operation sections to minimize the time for the breakdowns and for regular maintenance of lines and distribution transformers.

The APCPDCL is also taking steps to minimize the interruptions to consumers by providing HVDS system, which is having lower capacities of distribution transformers and decreasing the ratio of transformer to the consumer.

Providing of logic controllers for ensuring regulated hours of supply. In order to further stabilize the supply conditions in the primary distribution system 82Nos. 33/11KV sub stations, and distribution transformers are also proposed in the areas of over load and low voltage pockets. During this financial year 10Nos 33/11KV substaions are commissioned at Avuladatla in the constituency of  Rayadurg of Anantapur circle, Mogiligidda, Chowdariguda of Shadnagar constituency, Ravichedu of Kalwakurthy  constituency in Mahabubnagar  Circle, Yerraram of Devarakonda constituency, Settipalem, NG Bandalu of Aleru constituency in Nalgonda Circle Ramayapalli of Gajwel constituency of Medak Circle Siddaluru of Vikarabad constituency, Gundal of Parigi  constituency and Malkaram of Chevella Constituency in Ranga Reddy South Circle.

In addition to this, segregation of lighting load from Agl. load and extending 24 hrs lighting supply to villages, single phase distribution transformers are erected which resulted in good improvement in voltage levels.  106 Nos Rural feeders i.e., 41 Nos in Anantapur Circle, 33 Nos in Mahabubnagar Circle, 11 Nos in Nalgonda Circle, 18 Nos in Ranga Reddy North Circle and 3 Nos Ranga Reddy South Circle are identified and completed.

By this the number of breakdowns and interruptions have substantially reduced as the length of LT line is reduced.

In twin cities to reduce the interruptions on account of over head lines, UG cable system is proposed and so far about 60Km of 11kv/LT cable was laid and balance works are in progress. The other areas will be taken up in a phased manner. The UG cable system will drastically cut down the breakdowns.

The information relating to breakdowns and interruptions is monitored at Corporate office on daily basis by getting the information from all the control rooms of circles to the main control room in APCPDCL.

11 a.1)	 Number and Duration of Supply Interruptions on 33 KV and 11 KV networks. (Consolidated)

| Year | Month | No. of Interruptions |  | Duration in hours |  | No. of Breakdowns |  | Duration in hours |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 33 kV | 11 kV | 33 kV | 11 kV | 33 kV | 11 kV | 33 kV | 11 kV |
| 2004 | Apr | 1906 | 14322 | 2595 | 27782 | 94 | 903 | 501 | 3499 |
| 2004 | May | 1758 | 16229 | 1068 | 23972 | 90 | 971 | 299 | 3163 |
| 2004 | Jun | 1292 | 16936 | 1413 | 25162 | 68 | 995 | 463 | 3204 |
| 2004 | Jul | 2032 | 13280 | 1285 | 19880 | 70 | 842 | 217 | 3107 |
| 2004 | Aug | 1713 | 11924 | 1184 | 12555 | 60 | 537 | 121 | 1899 |
| 2004 | Sep | 5713 | 14047 | 189 | 2688 | 24 | 283 | 240 | 1809 |
| 2004 | Oct | 1180 | 17768 | 515 | 19030 | 169 | 961 | 112 | 2135 |
| 2004 | Nov | 997 | 13429 | 294 | 10867 | 86 | 691 | 58 | 1592 |
| 2004 | Dec | 772 | 17293 | 335 | 10934 | 93 | 647 | 62 | 1626 |
| 2005 | Jan | 1255 | 11647 | 652 | 19744 | 286 | 987 | 100 | 1827 |
| 2005 | Feb | 1644 | 10543 | 1071 | 9450 | 96 | 899 | 102 | 2182 |
| 2005 | Mar | 1563 | 11643 | 760 | 6756 | 166 | 853 | 306 | 1925 |
| 2005 | Apr | 517 | 3208 | 1188 | 7205 | 217 | 1080 | 378 | 2556 |
| 2005 | May | 797 | 3788 | 1890 | 6799 | 332 | 1193 | 606 | 3079 |
| 2005 | Jun | 566 | 1862 | 1644 | 5285 | 273 | 1312 | 434 | 3519 |
| 2005 | Jul | 737 | 2707 | 1227 | 7354 | 230 | 1274 | 359 | 3131 |
| 2005 | Aug | 453 | 4111 | 622 | 8661 | 215 | 1391 | 386 | 3949 |
| 2005 | Sep | 934 | 3697 | 406 | 4437 | 219 | 1192 | 195 | 2281 |

11. a . 2  33kv & 11kv Interruptions during 2004-2005

| Sl. No | Name of the Circle | 33KV System |  |  |  | 11KV System |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | No of feeders | Length of line in KM | No of Interruptions | Duration in Hours | No of feeders | Length of line in KM | No of Interruptions | Duration in Hours |
| 1 | Anantapur | 62 | 2076 | 9097 | 9079 | 485 | 10451 | 47940 | 76860 |
| 2 | Kurnool | 56 | 1939 | 833 | 75 | 408 | 9074 | 4929 | 421 |
| 3 | Mahabub nagar | 74 | 2080 | 4094 | 703 | 534 | 17349 | 30506 | 3657 |
| 4 | Nalgonda | 76 | 2208 | 473 | 733 | 672 | 14493 | 1119 | 1474 |
| 5 | Medak | 87 | 1576 | 6324 | 2234 | 551 | 7805 | 60640 | 93701 |
| 6 | RR South | 41 | 995 | 178 | 86 | 268 | 4643 | 16422 | 3459 |
| 7 | RR North | 31 | 341 | 617 | 572 | 212 | 1696 | 3635 | 10281 |
| 8 | Hyderabad | 83 | 172 | 922 | 226 | 426 | 2323 | 5450 | 8132 |
|  | Total | 510 | 11387 | 22538 | 13708 | 3556 | 67834 | 170641 | 197986 |

| Table 11.a.3 - 33 kV & 11 kV breakdowns during 2005-2006 (From 01-04-05 to 30-09-05) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| S. No. | Name of the Circle | 33 kV SYSTEM |  |  |  | 11 kV SYSTEM |  |  |  |
|  |  | No. of feeders | Length of lines Km | No. of breakdowns | Duration Hrs | No. of feeders | Length of lines Km | No. of breakdown | Duration Hrs |
| 1 | Anantapur | 63 | 2077 | 155 | 892 | 535 | 10614 | 446 | 2514 |
| 2 | Kurnool | 56 | 1939 | 48 | 236 | 408 | 92467 | 11 | 42 |
| 3 | Mahabubnagar | 77 | 2087 | 163 | 498 | 547 | 17381 | 1575 | 7419 |
| 4 | Nalgonda | 76 | 2208 | 69 | 203 | 672 | 14493 | 137 | 329 |
| 5 | Medak | 87 | 1576 | 21 | 47 | 551 | 7805 | 972 | 2184 |
| 6 | RR North | 32 | 345 | 80 | 141 | 215 | 1719 | 609 | 678 |
| 7 | RR South | 41 | 995 | 13 | 32 | 268 | 4643 | 302 | 354 |
| 8 | Hyderabad | 83 | 472 | 89 | 46 | 474 | 2604 | 1680 | 3421 |
|  | TOTAL | 515 | 11699 | 638 | 2096 | 3670 | 151726 | 5732 | 16941 |

## PERIODS WHEN VOLTAGE/FREQUENCY WAS BEYOND PRESCRIBED LIMITS

Requirement in the Guidelines:

Periods when voltage and/or frequency  was beyond the prescribed  limits on primary distribution ( 33KV, 11KV) networks. Details of steps proposed to improve performance and monitoring.  ( as given in Guidelines – 11b)

APCPDCL’s Response:

Voltage

The 400KV substations commissioned at Mamidipally and Kurnool have substantially contributed in improving power supply system as a whole.

In order to further stabilize the supply conditions in the primary distribution system during 2005-06, 82Nos 33/11KV Substations proposed. During this financial year 10Nos. During this financial year 10Nos 33/11KV substaions are commissioned at Avuladatla in the constituency of  Rayadurg of Anantapur circle, Mogiligidda, Chowdariguda of Shadnagar constituency, Ravichedu of Kalwakurthy  constituency in Mahabubnagar  circle, Yerraram of Devarakonda constituency,           NG Bandalu of Aleru constituency in Nalgonda circle Ramayapalli of Gajwel constituency of Medak circle Siddaluru of Vikarabad constituency, Gundal of Parigi  constituency and Malkaram of Chevella constituency in Ranga Reddy South circle.

Frequency:

Normally the grid  frequency is being maintained always above 49HZ only. In case of any disturbances load shedding is restored to regulate system frequency and at times. During system emergencies 132KV feeders are tripped to bring necessary load relief. The load dispatch center, at Vidyut Soudha controls the frequency emergencies giving instructions to 220KV and 132KV Substation operators for giving load relief on different feeders in all the circles. The load dispatch center will be in constant touch with generating stations to take necessary measures to maintain frequency.

## PENDING APPLICATIONS:

Requirement in the Guidelines:

Number of supply or connection applications pending for more than six months, categorized by the reasons why (Guidelines- 11 C).

CPDCL’s Response:

The CPDCL has taken steps for regular monitoring of the status of applications for new connections and initiated the processing of applications and releases through the customer service centers.    The new connections are provided as per the standards set by the Hon’ble Commission.

The provision of new connections under agricultural category is based on the guidelines / targets set by the Government of Andhra Pradesh.

The cause wise pendency of applications is as shown in the following tables:

| Table 11.c.1 - Number of connection applications pending more than six months as on 31-03-2005 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ATP | KNL | MBN | NLG | MDK | RRN | RRS | HDN | HDS | HDC | CPDCL |
| LT |  |  |  |  |  |  |  |  |  |  |  |
| CAT1 | 0 | 22 | 39 | 151 | 27 | 176 | 19 | 1673 | 0 | 4 | 2111 |
| CAT II | 0 | 36 | 5 | 52 | 13 | 6 | 6 | 191 | 0 | 3 | 312 |
| CAT III | 9 | 29 | 0 | 34 | 5 | 9 | 28 | 11 | 2 | 0 | 127 |
| CAT IV | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 |
| CAT V | 3459 | 1682 | 21658 | 8527 | 9542 | 0 | 6383 | 0 | 0 | 0 | 51251 |
| CAT VI | 0 | 70 | 0 | 89 | 0 | 0 | 37 | 0 | 0 | 0 | 196 |
| CAT VII | 0 | 237 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 251 |
| CAT VIII | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| HT |  |  |  |  |  |  |  |  |  |  |  |
| CAT I | 4 | 1 | 4 | 7 | 5 | 13 | 24 | 0 | 4 | 0 | 62 |
| CAT II | 1 | 0 | 0 | 2 | 0 | 2 | 7 | 10 | 10 | 7 | 39 |
| CAT IV | 0 | 3 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 11 |
| CAT V | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| CAT VI | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 4 |
| OTHERS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Total | 3473 | 2089 | 21710 | 8880 | 9592 | 206 | 6505 | 1885 | 16 | 16 | 54372 |

| Table 11.c.2 - Number of connection applications pending more than six months as on 30-09-2005 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ATP | KNL | MBN | NLG | MDK | RRN | RRS | HDN | HDS | HDC | CPDCL |
| LT |  |  |  |  |  |  |  |  |  |  |  |
| CAT1 | 0 | 25 | 143 | 286 | 0 | 203 | 23 | 1854 | 0 | 0 | 2534 |
| CAT II | 0 | 1 | 10 | 55 | 0 | 11 | 7 | 291 | 0 | 0 | 375 |
| CAT III | 11 | 37 | 3 | 58 | 2 | 2 | 36 | 38 | 4 | 0 | 191 |
| CAT IV | 2 | 5 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 9 |
| CAT V | 3039 | 3348 | 21328 | 8520 | 8961 | 0 | 6195 | 0 | 0 | 0 | 51391 |
| CAT VI | 6 | 32 | 0 | 74 | 0 | 0 | 13 | 1 | 0 | 0 | 126 |
| CAT VII | 0 | 59 | 0 | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 81 |
| CAT VIII | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| HT |  |  |  |  |  |  |  |  |  |  |  |
| CAT I | 2 | 3 | 19 | 25 | 7 | 80 | 17 | 0 | 2 | 0 | 155 |
| CAT II | 1 | 0 | 0 | 5 | 0 | 9 | 9 | 13 | 3 | 8 | 48 |
| CAT IV | 0 | 10 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 19 |
| CAT V | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| CAT VI | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 7 |
| OTHERS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Total | 3061 | 3521 | 21511 | 9034 | 8984 | 305 | 6301 | 2197 | 9 | 13 | 54936 |

Table 11.c.2 - Number of connection applications pending more than six months as on 31-03-2005

| Category |  | Formalities not completed by consumer |  | Being processed in office |  | For Want of material | Erection work in progress | Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LT Supply |  |  |  |  |  |  |  |  |
| Domestic |  | 1655 |  | 0 |  | 0 | 456 | 2111 |
| Non-domestic & Commercial |  | 223 |  | 0 |  | 0 | 89 | 312 |
| Industrial |  | 73 |  | 0 |  | 0 | 54 | 127 |
| Cottage industries |  | 8 |  | 0 |  | 0 | 0 | 8 |
| Agriculture |  | 46912 |  | 0 |  | 0 | 4339 | 51251 |
| Street lights & Water supply in local bodies |  | 117 |  | 0 |  | 0 | 79 | 196 |
| General purpose |  | 226 |  | 0 |  | 0 | 25 | 251 |
| Temporary supply |  | 0 |  | 0 |  | 0 | 0 | 0 |
| HT Supply |  |  |  |  |  |  |  |  |
| Category 1 |  | 55 |  | 0 |  | 0 | 7 | 62 |
| Category 2 |  | 31 |  | 0 |  | 0 | 8 | 39 |
| Category 4 |  | 7 |  | 0 |  | 0 | 4 | 11 |
| Category 5 |  | 0 |  | 0 |  | 0 | 0 | 0 |
| Category 6 |  | 4 |  | 0 |  | 0 | 0 | 4 |
| Others |  | 0 |  | 0 |  | 0 | 0 | 0 |
| Total |  | 49311 |  | 0 |  | 0 | 5061 | 54372 |
| Table 11.c.4 - Number of connection applications pending for more than six months as on 30-09-2005 |  |  |  |  |  |  |  |  |
| Category | Formalities not completed by consumer |  | Being processed in office |  | For Want of material |  | Erection work in progress |  |
| Domestic | 1936 |  | 0 |  | 0 |  | 598 |  |
| Non-domestic & Commercial | 283 |  | 0 |  | 0 |  | 92 |  |
| Industrial | 135 |  | 0 |  | 0 |  | 56 |  |
| Cottage industries | 9 |  | 0 |  | 0 |  | 0 |  |
| Agriculture | 46839 |  | 0 |  | 0 |  | 4552 |  |
| Street lights & Water supply in local bodies | 56 |  | 0 |  | 0 |  | 70 |  |
| General purpose | 11 |  | 0 |  | 0 |  | 70 |  |
| Temporary supply | 0 |  | 0 |  | 0 |  | 0 |  |
| HT Supply |  |  |  |  |  |  |  |  |
| Category 1 | 149 |  | 0 |  | 0 |  | 6 |  |
| Category 2 | 42 |  | 0 |  | 0 |  | 6 |  |
| Category 4 | 14 |  | 0 |  | 0 |  | 5 |  |
| Category 5 | 0 |  | 0 |  | 0 |  | 0 |  |
| Category 6 | 7 |  | 0 |  | 0 |  | 0 |  |
| Others | 0 |  | 0 |  | 0 |  | 0 |  |
| Total | 49481 |  | 0 |  | 0 |  | 5455 |  |

## ACCIDENTS

Requirement in Guidelines :

Number of reported fatal and non-fatal accidents for the year 2002 –2003 differentiating between accidents involving humans and those involving animals. An analysis of steps to reduce such accidents must also be provided (Guidelines – 11d)

Requirement in Guidelines :

Number of reported fatal and non-fatal accidents for the year 2003 –2004 differentiating between accidents involving humans and those involving animals. As analysis of steps to reduce such accidents must also be provided (Guidelines – 11d)

APCPDCL’ s Response

Data on the number of fatal and non-fatal accidents differentiated between accidents involving human and those involving animals are presented in Table 11d1. This data includes accidents in 33KV, 11KV and LT distribution network only. The total number of fatal and non fatal accidents recorded in APCPDCL in 2004 – 2005 is shown in the table below. The accident tally includes departmental staff, contract labour and members of genera public. The accidents involving general public shown in table 11d1.

Table 11.d1 – Fatal and Non-Fatal accidents :

| Category | Total No. of Accidents in 2004 – 05 |  |  | Total |
| --- | --- | --- | --- | --- |
|  | Departmental | Contract Labour | Public |  |
| Fatal |  |  |  |  |
| Human Beings | 10 | 14 | 181 | 205 |
| Animals | 0 | 0 | 44 | 44 |
| # Total | 10 | 14 | 225 | 249 |
| Non-Fatal |  |  |  |  |
| Human Beings | 22 | 11 | 45 | 78 |
| ## Animals | 0 | 0 | 0 | 0 |
| Total | 22 | 11 | 45 | 78 |

The details of accidents categorized under departmental and non-departmental functions. Table 11d2 summarize the number of fatal and non fatal accidents recorded various circles for the year 2004 – 2005.

# REASONS FOR NON-DEPARATMENTAL ACCIDENTS :

- Non availability of Guy Insulators to the stays.

- Snapping conductors of AAC/ACSR/Copper conductor of LT lines and 11KV lines on account of gales, cyclones and aging.

- Removal of stays by the public resulting in leaning of the dead-end poles and consequent sagging of the live lines / wires with reduced ground clearances.

- Dashing of lorries and other loaded vehicles against electric poles/stays resulting in snapping of the conductors or drooping of the live conductor etc.

- Falling of advertising boards on the live lines.

- Members of the public coming into contact or within arcing distance of live lines while carrying out work such as digging of bore wells. Assembling TV antennas or cutting the leaves of palm trees/coconut trees in the agricultural fields etc.,

- In the agriculture belt consumers are extending the supply by highly non standard service wires on wooden sticks and in a most substandard way. Public in most cases farmers only are getting electrocuted by touching the same wires whenever they are falling on the ground.

- Tampering with the electrical wiring by consumers trying to rectify faults in their own installations.

- Constructions of houses or multistoried buildings without maintaining proper clearances and set-back from existing live electrical lines or location of distribution transformer close to a building without maintaining mandatory electrical clearances.

Animals and cattle rearers are the worst hit among others in the non-departmental accidents, as they do not notice the loose or fallen electrical lines subsequent to a gale or storm. There is a need for the villagers to be alerted and properly educated in the local villages.

All the line patrolling staff carry out immediate rectification of the snapped lines or conductors and damaged or learning poles particularly in village areas. A proper record or log book is maintained by them during their patrolling duties which is reviewed and any defects noticed by them Viz. Bottom rusted poles, conductor with out proper supports rectified to avoid accidents after such calamities like gales etc.

REASONS FOR DEPARTMENTAL ACCIDENTS :

- Non observance of safety rules.

- Non utilisation of safety appliances by the workmen though they are supplied and trained to use them.

- Non-operation of one of the blades of Air Break (AB) switches due to bad maintenance, leading to arcing and burn injuries.

- Slipping from poles and O/H lines while on work due to non-utilisation of safety belt.

- Attending of fuse off calls complaints on the poles without using proper safety gloves etc.

- Due to improper co-ordination and communication of line clearance or improper earthing of the line or equipment at the work spot.

- Due to negligence or by over confidence to visually ensure that the AB switch is kept open while undertaking renewal or replacement of a Blown Horn Gap (HG) fuse.

- While working carelessly on the bottom portion of rusted rail poles. R.S. Joists or damaged PSCC/RCC poles in the ground, which cannot be easily detected.

- Working at double feed points without working knowledge of the feeding arrangements and without ensuring that there is no back – feeding or charged condition of line.

- Allowing un-authorized persons to work on lines.

Table 11.d 2 statement showing Fatal / Non-Fatal accidents to general public / animals during the period from 01.04.2004 -31.03.2005.

| Sl.No | Name of the Circle | Human |  | Animals |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Fatal | Non-Fatal | Fatal | Non-Fatal |
| 1 | Anantapur | 41 | 14 | 5 | 0 |
| 2 | Kurnool | 40 | 16 | 12 | 0 |
| 3 | Mahabubnagar | 27 | 4 | 2 | 0 |
| 4 | Nalgonda | 22 | 7 | 9 | 0 |
| 5 | Medak | 21 | 5 | 10 | 0 |
| 6 | Ranga Reddy – South | 22 | 17 | 5 | 0 |
| 7 | Ranga Reddy – North | 26 | 3 | 1 | 0 |
| 8 | Hyd – North | 4 | 3 | 0 | 0 |
| 9 | Hyd – Central | 7 | 4 | 0 | 0 |
| 10 | Hyd – South | 4 | 5 | 0 | 0 |
| 11 | SCADA | 1 | 0 | 0 | 0 |
|  | A.P.C.P.D.C.L | 205 | 78 | 44 | 0 |

REMEDIAL ACTION TO REDUCE ACCIDENTS:

- Almost all fatal or non fatal accident cases have been due to electrocution of humans or animals by coming into contact with live conductors. In some cases the live conductors were found to have improper ground clearances. Some of the accidents were also cause due to conductors snapping but continuing to be live. There have also been cases where the stay wire or poles have inadvertently become energise due to improper earthing absence of guy insulator etc. In the accidents occurred to the farmers, it is generally observed that the cause of accidents are due to using of un-standard service wires or not taking proper care while switching off and switching on the starters of the motors. In some cases it is observed that lifting of the pipes without noticing the overhead lines. In Urban areas the plumbers and centring workers while working at the construction of buildings are becoming victims of electrocution due to touching the lines passing over the buildings or by the side of the buildings while carrying the rods and pipes etc. In some cases, it is also observed that the lorry drivers are parking their vehicles underneath the lines and climbing the lorry cabin and by oversight coming in touch with live lines and becoming the victims of electric accidents. To reduce the departmental and non-departmental accidents, the following remedial measures are being taken.

- Standard construction practice to be ensured whenever new distribution lines are laid and energised.

- Raising of plinths and DTR boxes to prevent touching of live lines by human beings as well as animals.

- Providing fencing to major DTR structures to prevent for touching by human beings and animals.

- An alerting mechanism to be arranged in liasion with villages well in advance of charging any new distribution line. Distribution pamphlets and making loud speaker announcements making Tom Tom in villages may also be restored to as an added precautionary measure.

- Clearances for O/H lines as specified in IE rules 77,78,79 and 80 to be strictly maintained and verified at the time of statutory inspections of lines & substations before charging.

- Even RCC / PSCC poles used in the rural areas must be earthed with pig tailed    GI wire.

- Guy insulators for stay wire be provided to prevent inadequate energisation.

- Anti-climbing devices may be provided to prevent people from scaling towers or poles.

- Foot cross arms may be provided at least for angle points and cut points for isolation.

- All LT tapping poles are to be provided with sectionalise fuses along with arial boards for services.

- Double feed LT lines may be cautioned with boards, as well as by creating a dead span.

- Neutral for each DTR along with street light phase may be insisted for each DTR, so that street light phase is limited to distribution transformer wise.

- Safety equipment and material (T&P) are procured and provided to all Circles in APCPDCL.

- Rubber gloves and gant belts.

- Safety belts.

- Helmet

- Discharge earth rods.

- Insulated tools like cutting pliers, screw drivers, bamboo ladders etc.

Special ladder with fiber glass rails are procured and provided in twin cities to attend breakdowns.

- Classes are being conducted for the workmen on payday or any suitable working day to enlighten them on safety measures and to avoid electrical accidents by proper utilisation of safety devices and precautions as per the safety rules. The category of employees generally involved in the departmental accidents are of the following category.

- Helpers.

- A.L.M’s

- Linemen.

- Electrical safety week was observed in CPDCL from 01.05.2003 to 07.05.2003. During this period medical checkups were arranged to O&M staff and contract labour and their families in all divisions of CPDDCL and message was given to use safety appliances while working on electric lines to avoid electrical accidents.

- Deterrent action taken against all the erring field staff who fail to take safety precautions while working on lines and also ensure that adequate quantity of safety appliances are made available to all the concerned staff members. Safety training courses are regularly conducted.

### INADEQUATE AND DEFECTIVE METERS:

Requirement in Guidelines:

Number of inadequate and defective meters, programme and phasing of investment for replacement. (Guidelines-11 e).

CPDCL’s Response:

All steps are taken in CPDCL to maintain required stocks of meters to cater for the release of new connections and for immediate replacement of defective meters reported.

The status of the defective meters during the year 2004-05 is indicated below:

Table 11.e.1 - Stuck up Meters -  2004-05

| Circle | Stuck up on 1.4.2004 |  |  | Stuck up during 2004-05 |  |  | Replaced during 2004-05 |  |  | Stuck up as on 1.4.2005 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 Ph | 3 Ph | Total | 1 Ph | 3 Ph | Total | 1 Ph | 3 Ph | Total | 1 Ph | 3 Ph | Total |
| Anantapur | 1115 | 430 | 1545 | 24987 | 981 | 25968 | 24013 | 715 | 24728 | 2089 | 696 | 2785 |
| Kurnool | 404 | 6 | 410 | 65969 | 2060 | 68029 | 66023 | 2058 | 68081 | 350 | 8 | 358 |
| Mahaboobnagar | 8452 | 363 | 8815 | 21241 | 595 | 21836 | 17170 | 560 | 17730 | 12523 | 398 | 12921 |
| Nalgonda | 27904 | 315 | 28219 | 20894 | 1742 | 22636 | 37028 | 1256 | 38284 | 11770 | 801 | 12571 |
| Medak | 8546 | 298 | 8844 | 6969 | 127 | 7096 | 12391 | 359 | 12750 | 3124 | 66 | 3190 |
| Ranga Reddy-N | 538 | 8 | 546 | 8491 | 1809 | 10300 | 8931 | 1812 | 10743 | 98 | 5 | 103 |
| Ranga Reddy - S | 5260 | 8 | 5268 | 12073 | 45 | 12118 | 11780 | 49 | 11829 | 5553 | 4 | 5557 |
| Hyd-North | 81 | 40 | 121 | 7917 | 2658 | 10575 | 7963 | 2689 | 10652 | 35 | 9 | 44 |
| Hyd-Central | 410 | 102 | 512 | 4351 | 1553 | 5904 | 4679 | 1599 | 6278 | 82 | 56 | 138 |
| Hyd-South | 182 | 17 | 199 | 2287 | 102 | 2389 | 2342 | 117 | 2459 | 127 | 2 | 129 |
| TOTAL | 52892 | 1587 | 54479 | 175179 | 11672 | 186851 | 192320 | 11214 | 203534 | 35751 | 2045 | 37796 |

Table 11.e.2 - Burnt Meters -  2004-05

| Circle | BurntMeters as on 1.4.2004 |  |  | Burnt during 2004-05 |  |  | Replaced during 2004-05 |  |  | Burnt Meters as on 1.4.2005 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 Ph | 3 Ph | Total | 1 Ph | 3 Ph | Total | 1 Ph | 3 Ph | Total | 1 Ph | 3 Ph | Total |
| Anantapur | 363 | 29 | 392 | 2514 | 347 | 2861 | 1656 | 267 | 1923 | 1221 | 109 | 1330 |
| Kurnool | 189 | 3 | 192 | 7222 | 409 | 7631 | 7355 | 406 | 7761 | 56 | 6 | 62 |
| Mahaboobnagar | 1285 | 74 | 1359 | 4023 | 179 | 4202 | 2275 | 84 | 2359 | 3033 | 169 | 3202 |
| Nalgonda | 1046 | 10 | 1056 | 482 | 43 | 525 | 744 | 53 | 797 | 784 | 0 | 784 |
| Medak | 1380 | 55 | 1435 | 8397 | 161 | 8558 | 4710 | 208 | 4918 | 5067 | 8 | 5075 |
| RR - North | 5 | 0 | 5 | 2483 | 385 | 2868 | 2486 | 385 | 2871 | 2 | 0 | 2 |
| RR - South | 875 | 5 | 880 | 2292 | 34 | 2326 | 1892 | 37 | 1929 | 1275 | 2 | 1277 |
| Hyd-North | 37 | 21 | 58 | 1742 | 791 | 2533 | 1767 | 809 | 2576 | 12 | 3 | 15 |
| Hyd- Central | 59 | 8 | 67 | 1276 | 317 | 1593 | 1272 | 320 | 1592 | 63 | 5 | 68 |
| Hyd- South | 18 | 2 | 20 | 975 | 48 | 1023 | 959 | 47 | 1006 | 34 | 3 | 37 |
| TOTAL | 5257 | 207 | 5464 | 31406 | 2714 | 34120 | 25116 | 2616 | 27732 | 11547 | 305 | 11852 |

Table 11.e3 – Defective Meters -  2004-05

| Circle | Defective Meters as on 1.4.2004 |  |  | Defective during 2004-05 |  |  | Replaced during 2004-05 |  |  | Defective Meters as on 1.4.2005 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 Ph | 3 Ph | Total | 1 Ph | 3 Ph | Total | 1 Ph | 3 Ph | Total | 1 Ph | 3 Ph | Total |
| Anantapur | 1478 | 459 | 1937 | 27501 | 1328 | 28829 | 25669 | 982 | 26651 | 3310 | 805 | 4115 |
| Kurnool | 593 | 9 | 602 | 73191 | 2469 | 75660 | 73378 | 2464 | 75842 | 406 | 14 | 420 |
| Mahaboobnagar | 9737 | 437 | 10174 | 25264 | 774 | 26038 | 19445 | 644 | 20089 | 15556 | 567 | 16123 |
| Nalgonda | 28950 | 325 | 29275 | 21376 | 1785 | 23161 | 37772 | 1309 | 39081 | 12554 | 801 | 13355 |
| Medak | 9926 | 353 | 10279 | 15366 | 288 | 15654 | 17101 | 567 | 17668 | 8191 | 74 | 8265 |
| RR - North | 543 | 8 | 551 | 10974 | 2194 | 13168 | 11417 | 2197 | 13614 | 100 | 5 | 105 |
| RR - South | 6135 | 13 | 6148 | 14365 | 79 | 14444 | 13672 | 86 | 13758 | 6828 | 6 | 6834 |
| Hyd-North | 118 | 61 | 179 | 9659 | 3449 | 13108 | 9730 | 3498 | 13228 | 47 | 12 | 59 |
| Hyd- Central | 469 | 110 | 579 | 5627 | 1870 | 7497 | 5951 | 1919 | 7870 | 145 | 61 | 206 |
| Hyd- South | 200 | 19 | 219 | 3262 | 150 | 3412 | 3301 | 164 | 3465 | 161 | 5 | 166 |
| TOTAL | 58149 | 1794 | 59943 | 206585 | 14386 | 220971 | 217436 | 13830 | 231266 | 47298 | 2350 | 49648 |

## UNAUTHORISED CONNECTIONS:

Requirement in Guidelines:

Number of unauthorized connections (as a result of sample survey) to be reported by tariff category.  Measures adopted to curb unauthorized consumption.  Results and programme for the future.  (Guidelines – 11 f).

APCPDCL’s Response

Regular inspections are being conducted in CPDCL by the operations and the DPE wings, with the assistance of the vigilance wing for identifying and curbing unauthorized consumption.

The status of inspections and cases booked is given below:

Table 11 f : Number of services inspected and booked for unauthorized use during each of the months from October 2004 to September 2005.

| Month | Inspected | Booked |
| --- | --- | --- |
| October-04 | 50548 | 3034 |
| November-04 | 48785 | 4163 |
| December-04 | 58818 | 4170 |
| January-05 | 58559 | 3945 |
| February-05 | 63933 | 4782 |
| March-05 | 57129 | 3781 |
| April-05 | 57306 | 3193 |
| May-05 | 48340 | 4268 |
| June-05 | 59803 | 4037 |
| July-05 | 59486 | 4146 |
| August-05 | 59365 | 3810 |
| September-05 | 57397 | 4297 |

## REVENUE ARREARS:

Requirement in Guidelines:

Amount of revenue arrears at beginning and end of year analysed age wise on a six monthly basis.  Reasons for non-collection and details of litigation involving collection of revenue of Rs.50,000 or more should also be provided (Guide Lines 11 – g).

APCPDCL’s Response:

The following tables illustrate the arrears position of APCPDCL as on 31-3-2005.

| Schedule 11 g1 |  |
| --- | --- |
| Break-up of arrears on various accounts as on 31-03-2005. |  |
|  | Rs. Lakhs |
| Live services | 32166.50 |
| State Government Departments | 258.83 |
| State Government Undertakings | -179.69 |
| Central Govt., Depts/Undertakings | 15635.52 |
| Local Bodies | 629.90 |
| Court Cases | 13427.97 |
| Disconneted services | 35112.98 |
| Debts decreed to be withdrawn | 795.14 |
| Others (RR-Act, RESCO & Others) | 10017.16 |
| Net Arrears | 107864.32 |

| Schedule 11g2 |  |
| --- | --- |
| Category wise arrears as on 31-03-2005. |  |
| LT Category | Rs. Lakhs |
| LT Cat-I Domestic | 46280.37 |
| LT Cat-II Non-Domestic | 6221.00 |
| LT Cat-III Normal Industrial | 4469.73 |
| LT Cat-IV Cottage Ind. | 68.24 |
| LT Cat-V Agricultural | 2002.07 |
| LT Cat-VI Steet Lights | 2263.17 |
| LT Cat-VII General Purpose | 712.97 |
| LT Cat-VIII Temporary Supply | 71.19 |
| LT Total | 62088.74 |
| HT Category | Rs. Lakhs |
| HT Cat-I Indutrial | 35637.94 |
| HT Cat-II Non-Industrial | 1743.90 |
| HT Cat-IV Agricultural (IV A) | -183.11 |
| HT Cat-V Railway Traction | 259.07 |
| HT Cat-VI Residential | -276.54 |
| RESCO | 8608.09 |
| HT Temp. Supply | -13.78 |
| HT Total | 45775.57 |
| LT + HT TOTAL | 107864.31 |
| NOTE:-Unbilled revenue and provison for bad debts not taken into account. |  |

Schedule  11 g3

| Schedule 11g3 |  |
| --- | --- |
| Ageing Analysis of receivables |  |
| Total for the LT | Rs. Lakhs |
| Duration | As on 31-03-05 |
| 3-6 months old | 14150 |
| 6-12 months old | 9465 |
| More than 12 months old | 38474 |
| Total | 62089 |
| Total for the HT | Rs. Lakhs |
| Duration | As on 31-03-05 |
| 3-6 months old | 18211 |
| 6-12 months old | 12409 |
| More than 12 months old | 15156 |
| Total | 45776 |
| Total for the LT + HT | Rs. Lakhs |
| Duration | As on 31-03-05 |
| 3-6 months old | 32361 |
| 6-12 months old | 21874 |
| More than 12 months old | 53630 |
| Total | 107865 |

Detailed list of consumers having Rs. 50,000 or more arrears as on September 30, 2005 is already placed in the company website.

### INITIATIVES TAKEN TO REALISE THE ARREARS:

- To have a realistic analysis of collectable and un-collectable arrears outstanding as on 31-03-2004, audit of receivable has been assigned for age-wise analysis of LT and HT services and to assess recovery potential of c.c.charges arrears due.

- In the fortnightly videoconferences with the Superintending Engineers / Opns, the disconnection of services whose arrears are more than Rs 5000 are being reviewed. At the end of every month, the disconnections of HT services who have not paid their monthly CC charges is also reviewed.

- The CAT analysis having list of F-class services is being sent to the subdivisions every month for review and disconnections.

- Sanction of installment facility LT II, III and HT I ,II has been withdrawn from the field offices so that there will not be further addition to the arrears.

- Pursuing the Government heads of the departments for realization of C.C charges dues. The c.c.charges arrears in respect of Govt Department Departments, Municipalities and Panchayats are being received through centralized payments made by the Govt. of A.P.

- Organizing the special drives for collection of arrears and physical verification of services under disconnection (UDC) duly ensuring the defaulting consumers are not availing supply through link services or other means.

- 100% implementation of issue of ‘D’ list and operation in respect finalised cases of theft & malpractices and back billing cases. This is also being pursued while holding video conferences regularly for effective monitoring.

- Issue of one month notices to Under Disconnection Services (UDC) as per B.P.Ms.No.151 & terminate the agreement duly adjusting the Consumption Deposit against the C.C charges dues.  Organised disconnection of link services of the already disconnected services for realization of arrears outstanding.

- Implementation of RR Act to recover the long pending dues by deploying the Dy. Tahasildars from Revenue Department. A substantial amount has been recovered through the efforts.

10.	 Arrears under Court cases have been pursued and got disposed in favour of the company and realization process is under progress. Monthly meetings are being held with the concerned accounts and legal officers to monitor the court cases. In the cases where the amount is high, senior advocates are being engaged.

## METER READING AND COLLECTION

Requirement in Guidelines:

Data should be provided for each consumer category indicating (i) the normal meter reading cycle and the number of meter reading not carried out in accordance with the cycle and (ii) the number of consumer bills not served within 15 days of the meter reading.  Please also provide details of plans to improve the efficiency and punctuality of meter reading, the dispatch of consumer bills and cash collection. (Guidelines 11 g-contd).

APCPDCL’s Response

APCPDCL is arranging the Meter Reading of all the Metered Services as follows:

Table 11.g.4 – MBC Schedule

| I. Domestic II Non-Domestic VII General Purpose | Meter reading, Billing & Collection (MBC) is done bi-monthly rural consumers and monthly billing is done in all Towns, Muncipalities and mandal head quarters through Hand held Computer billing machines. High value monthly billing is done all over the DISCOM |
| --- | --- |
| III Industrial IV Cottage Industries VI Street Lights & PWS | Meter reading, Billing & Collection (MBC) is done monthly. |
| V Agriculture | Billing is done as per the meter readings and slab system commensurate with the connected load as per the Tariff Order. Pass Books are issued to the consumers duly indicating the amount payable to the Agl consumers. Since, Govt. of A.P. is paying the c.c.charges for providing free power supply to this category consumers , the DISCOM is issuing half yearly bills to the consumers for collection of customer charges. |
| All the HT Categories | The Billing is done monthly for all categories. Meter reading is done monthly for all Categories. Collection is done for all categories on a monthly basis. |

APCPDCL has achieved substantial progress in the matter of collection of the revenues over the past few years and the overall collection efficiency has improved.  In respect of the meter reading default  cases, the following data is furnished for information of the Hon’ble Commission.

Table 11.g.5 – Meter Reading Defaults

| Month | Total Services | RNF Cases | Percentage (%) |
| --- | --- | --- | --- |
| April-05 | 4363243 | 6575 | 0.15 |
| May-05 | 4458175 | 9633 | 0.22 |
| June-05 | 4690108 | 12348 | 0.26 |
| July-05 | 4418327 | 11142 | 0.25 |
| Aug-05 | 4421838 | 5332 | 0.12 |
| Sep-05 | 4292873 | 8126 | 0.19 |

In the matter of Bill Distribution, APCPDCL made pioneering efforts to eliminate the defaults and consequent complaints in this regard and commenced the Spot Billing System in the Twin Cities and Municipalities of Rangareddy District from November, 2001onwards on a regular basis.  APCPDCL has also started the Spot Billing System in the other district from January, 2002 onwards. All the   Mandals and Villages are covered by Spot Billing System and bills are being issued  on bi-monthly basis. Monthly Spot Billing System with the handheld Computer devices is covered in all the Municipalities and Towns of the DISCOM.  The Spot Billing System has almost eliminated the complaints of non-receipt of the bills and reading not furnished cases.